## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  |  | 1849 | 0 | 1440 |  | 409 | #DIV/0! | 22.12%
RTU-2 |  |  | 1811 | 0 | 1390 |  | 421 | #DIV/0! | 23.25%
RTU-3 |  |  | 2497 | 0 | 1994 |  | 503 | #DIV/0! | 20.14%
MUA-1 | [10 empty] | 2268
EF-1 | [12 empty] | 1759
EF-2 | [12 empty] | 1253
EF-3 | [14 empty] | 52
TOTALS |  | 0 | 6157 | 0 | 4824 | 0 | 1333 |  |  | 0 | 2268 | 0 | 3012 | 0 | 52
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 0 | 3601 |  | FRONT |  | 0.0053 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 0 | 3064 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 537 |  | REAR |  | 0.0073 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0063 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0