## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 1600 | 1532 | 1250 | 1197 | 350 | 335 | 21.88% | 21.87%
RTU-2 |  | 2400 | 2511 | 1900 | 2043 | 500 | 468 | 20.83% | 18.64%
RTU-3 |  | 2400 | 2343 | 1900 | 1837 | 500 | 506 | 20.83% | 21.6%
MUA | [9 empty] | 1200 | 1018
KEF-1 | [11 empty] | 700 | 700
KEF-2 | [11 empty] | 803 | 803
KEF-3 | [11 empty] | 718 | 718
EF-4 | [13 empty] | 39 | 39
EF-5 | [13 empty] | 57 | 57
TOTALS |  | 6400 | 6386 | 5050 | 5077 | 1350 | 1309 |  |  | 1200 | 1018 | 2221 | 2221 | 96 | 96
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2550 | 2327 |  | FRONT |  | -0.0255 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 2317 | 2317 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 233 | 10 |  | REAR |  | -0.0364 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.03095 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0