## SUMMARY (2)
AS FOUND - INITIAL AIR BALANCE SCHEDULE
|  | HVAC SUPPLY |  | DEVIATION | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | PASS / FAIL | DESIGN | ACTUAL | 110%-90% | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FAIL | 2000 | 956 | 47.8% | 1600 | 582 | 400 | 374 | 20% | 39.12%
RTU-2 | FAIL | 3000 | 1525 | 50.83% | 2400 | 1132 | 600 | 393 | 20% | 25.77%
RTU-3 | FAIL | 2000 | 937 | 46.85% | 1600 | 544 | 400 | 393 | 20% | 41.94%
MUA-1 | FAIL |  |  | 53.36% | [6 empty] | 1250 | 667
KEF1-GRIDDLE | FAIL |  |  | 77.87% | [8 empty] | 750 | 584
KEF2-TOASTER | FAIL |  |  | 158% | [8 empty] | 1000 | 1580
KEF3-FRYER | FAIL |  |  | 119.2% | [8 empty] | 750 | 894
EF1 | FAIL |  |  | 52% | [10 empty] | 75 | 39
EF2 | FAIL |  |  | 76% | [10 empty] | 75 | 57
TOTALS |  | 7000 | 3418 | 48.83% | 5600 | 2258 | 1400 | 1160 |  |  | 1250 | 667 | 2500 | 3058 | 150 | 96
NET BUILDING AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [8 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2650 | 1827 |  |  | FRONT |  | 0.012 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2650 | 3154 |  |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | -1327 |  |  | REAR |  | -0.021 | [8 empty] | TRUE
[6 empty] | AVERAGE |  | -0.0045 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
RTU1 OA FILTER DIRTY, DAMPER 100%OPEN, WITH FILTER OUT THE OA IS 1298, RTU 2 SAME/ FILTERS REMOVED OA = 688, MUA FILTERS ARE DIRTY ONCE REMOVED THE MUA-OA IS 1086
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT |  |  | FILTER TYPE/#/SIZE |  |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD |  |  | SOLO 9 16X16 |  |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250