## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
VRF-1 | OFFICE/FITTING | 1200 | 1168 | 1030 | 991 | 170 | 177 | 14.17% | 15.15%
VRF-12 | STOCK | 750 | 812 | 120 | 171 | 630 | 641 | 84% | 78.94%
VRF-13 | STOCK | 1300 | 1401 | 300 | 419 | 1000 | 982 | 76.92% | 70.09%
VRF-14 | STOCK | 1300 | 1425 | 300 | 402 | 1000 | 1023 | 76.92% | 71.79%
EF-1 | RESTROOMS | [12 empty] | 275 | 254
TOTALS |  | 4550 | 4806 | 1750 | 1983 | 2800 | 2823 |  |  | 0 | 0 | 0 | 0 | 275 | 254
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2823 |  | FRONT |  | 0.0189 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 275 | 254 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 2525 | 2569 |  | REAR |  | 0.0157 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0173 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0