## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FCU-1 | DINING | 1375 | 1406 | 1125 | 1406 | 250 |  | 18.18% | 0%
FCU-2 | DINING | 1375 | 1328 | 1125 | 1328 | 250 |  | 18.18% | 0%
FCU-3 | KITCHEN | 1375 | 1424 | 1165 | 1424 | 210 |  | 15.27% | 0%
FCU-4 | KITCHEN | 1375 | 1428 | 1165 | 1428 | 210 |  | 15.27% | 0%
KEF-1 | KITCHEN/RR | [12 empty] | 640 | 634
TOTALS |  | 5500 | 5586 | 4580 | 5586 | 920 | 953 |  |  | 0 | 0 | 0 | 0 | 640 | 634 | TRUE | FALSE | FALSE
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | TRUE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 920 | 953 |  | FRONT |  | -0.0051 | [8 empty] | TRUE
TOTAL EXHAUST |  | 640 | 634 |  | SIDE |  | -0.0017 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 280 | 319 |  | REAR |  | -0.0023
[5 empty] | AVERAGE |  | -0.0030333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Building has second store attached.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0