## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 2000 | 2184 | 1700 | 1868 | 300 | 316 | 15% | 14.47%
RTU-2 |  | 2000 | 2135 | 1700 | 1828 | 300 | 307 | 15% | 14.38%
RTU-3 |  | 4000 | 3728 | 3400 | 3728 | 600 | 0 | 15% | 0%
MUA-1 | [9 empty] | 2350 | 0
EF-1 | [11 empty] | 3600 | 3670
EF-2 | [13 empty] | 150 | 0
TOTALS |  | 8000 | 8047 | 6800 | 7424 | 1200 | 623 |  |  | 2350 | 0 | 3600 | 3670 | 150 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3550 | 623 |  | FRONT |  | 7e-05 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 3750 | 3670 |  | SIDE |  | 0.004 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | -200 | -3047 |  | REAR |  | 0.00054 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0015367 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
ACPSP CLOGGED PREVENTING AIR FLOW TO SPACE
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0