## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 6190 | 4450 | 4400 | 1700 | 1790 | 27.64% | 28.92%
RTU-2 | KITCHEN | 6150 | 5720 | 4475 | 4111 | 1675 | 1609 | 27.24% | 28.13%
PRV-2 | HOOD 1 | [10 empty] | 1500 | 1056
PRV-3 | HOOD 2 | [10 empty] | 1500 | 1458
PRV-1 | RESTROOM | [12 empty] | 300 | 313
EF1 | MOP ROOM | [12 empty] | 75 | 70
TOTALS |  | 12300 | 11910 | 8925 | 8511 | 3375 | 3399 |  |  | 0 | 0 | 3000 | 2514 | 375 | 383
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3375 | 3399 |  | FRONT |  | 0.0068 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3375 | 2897 |  | SIDE |  | 0.0076 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 502 |  | REAR |  | 0.0031 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0058333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0