## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9107 | 7800 | 7500 | 1700 | 1607 | 17.89% | 17.65%
AC-2 | DINING A | 2500 | 2981 | 1975 | 2333 | 525 | 648 | 21% | 21.74%
AC-3 | DINING B | 4175 | 3896 | 3175 | 2944 | 1000 | 952 | 23.95% | 24.44%
AC-4 | DINING B | 2765 | 2972 | 2165 | 2328 | 600 | 644 | 21.7% | 21.67%
AC-5 | PLAY AREA | 1800 | 1669 | 1500 | 1348 | 300 | 321 | 16.67% | 19.23%
AC-6 | BOH | 1200 | 1138 | 1080 | 1026 | 120 | 112 | 10% | 9.842%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1869
EF-2 | HOOD 2 | [10 empty] | 701 | 670
EF-3 | RESTROOM | [12 empty] | 500 | 547
EF-4 | HOOD 3 | [10 empty] | 390 | 408
TOTALS |  | 21940 | 21763 | 17695 | 17479 | 4245 | 4284 |  |  | 0 | 0 | 3003 | 2947 | 500 | 547
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4245 | 4284 |  | FRONT |  | 0.0027 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3503 | 3494 |  | SIDE |  | 0.0105 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 742 | 790 |  | REAR |  | 0.0013 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0048333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390