## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 | 8179 | 6375 | 6435 | 1750 | 1744 | 21.54% | 21.32%
AC-2 | MEAL FULFILLMENT | 4375 | 4348 | 3825 | 3770 | 550 | 578 | 12.57% | 13.29%
AC-3 | DINING | 6400 | 6550 | 4600 | 4805 | 1800 | 1745 | 28.12% | 26.64%
AC-4 | BOH | 1750 | 1745 | 1325 | 1340 | 425 | 405 | 24.29% | 23.21%
AC-5 | PLAY AREA | 1200 | 1179 | 1000 | 964 | 200 | 215 | 16.67% | 18.24%
EF-1 | KITCHEN HD 1 | [10 empty] | 1913 | 1785
EF-2 | KITCHEN HD 2&3 | [10 empty] | 1402 | 1337
EF-3 | RESTROOM | [12 empty] | 300 | 295
TOTALS |  | 21850 | 22001 | 17125 | 17314 | 4725 | 4687 |  |  | 0 | 0 | 3315 | 3122 | 300 | 295
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4725 | 4687 |  | FRONT |  | 0.03 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 3417 |  | SIDE |  | 0.01 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1110 | 1270 |  | REAR |  | 0.02 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.02 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390