## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
DOAS-1 | KITCHEN | 2300 | 2154 | 0 | 0 | 2300 | 2154 | 100% | 100%
DOAS-2 | DINING | 4400 | 4548 | 2900 | 2949 | 1500 | 1599 | 34.09% | 35.16%
EF-1 | HOOD2 FRY | [10 empty] | 1852 | 1907
EF-2 | HOOD1 GRILL | [10 empty] | 1662 | 1622
EF-3 | RESTROOMS | [12 empty] | 225 | 220
TOTALS |  | 6700 | 6702 | 2900 | 2949 | 3800 | 3753 |  |  | 0 | 0 | 3514 | 3529 | 225 | 220
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3800 | 3753 |  | FRONT |  | 0.0006 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3739 | 3749 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 61 | 4 |  | REAR |  | 0.0009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00075 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0