## 2EP-2925
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
TRANE | YHC072F3RMAOCHO | 155311361L | RTU-1 | KITCHEN | 500 | 583 | 0 | 0 | 1668 | 983 | 1 | 210.5 | 3 | 5 | 4.28 | 4.16 | 0.856 | 0.832 | -2.804%
TRANE | YHC102F3RHA09HOC | 155211520L | RTU-2 | DINING | 1000 | 0 | 1000 | 957 | 2.17V | 2.17V | 3.8 | 210.9 | 3 | 8.3 | 4.41 | 4.09 | 2.019 | 1.8725 | -7.256%
CAPTIVE-AIRE | A1-D.250-G10 | 2442668 | MUA-1 | HOOD 1 | 1775 | 560 | 1500 | 1071 | 1790/1753 | 948/1507 | 2 | 210.8 | 3 | 5.9 | 2.63 | 3.54 | 0.89153 | 1.2 | 34.6%
CAPTIVE-AIRE | NCA24HPFA | 2442668 | EF-1 | HOOD 1 | 2925 | 2682 | 2200 | 2143 | 1769/1759 | 873/734 | 1 | 211.1 | 3 | 5.9 | 3.5 | 2.99 | 0.59322 | 0.50678 | -14.57%
NL - NOT TESTED |  |  | EF-2 | RESTROOM | 150 | 150 | 150 | 150 | [10 empty] | #DIV/0!
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3275 | 1143 | 2500 | 2028 | -0.004 | FRONT DOOR | 3.3598 | 1143 | INITIAL
|  |  | TOTAL EXHAUST |  | 3075 | 2832 | 2350 | 2293 | -0.007 | BACK DOOR | 3.4113 | 2028 | FINAL
|  |  | NET AIRFLOW |  | 200 | -1689 | 150 | -265 | -0.0055 | AVERAGE | 1.534% | -885 | NET CHANGE

## 2EP-3200
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
TRANE |  |  | RTU-1 | KITCHEN | 500 |  | 0 |  |  | 890 / 790 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
TRANE |  |  | RTU-2 | DINING | 1000 |  | 1000 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
CAPTIVE-AIRE |  |  | MUA-1 | HOOD 1 | 1950 |  | 1875 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
CAPTIVE-AIRE |  |  | EF-1 | HOOD 1 | 3200 | 0 | 2650 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
NL - NOT TESTED |  |  | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3450 | 0 | 2875 | 0 |  | FRONT DOOR | #DIV/0! | 0 | INITIAL
|  |  | TOTAL EXHAUST |  | 3350 | 150 | 2800 | 150 |  | BACK DOOR | #DIV/0! | 0 | FINAL
|  |  | NET AIRFLOW |  | 100 | -150 | 75 | -150 |  | AVERAGE | #DIV/0! | 0 | NET CHANGE