## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 800 | 827 | 350 | 313
RTU-2 | SALES | 800 | 841 | 350 | 320
RTU-3 | BOH/KITCHEN | 800 | 779 | 350 | 333
EF-1 | WOMEN'S RR |  |  |  |  | 225 | 242 | 225 | 242
EF-2 | MEN'S RR |  |  |  |  | 525 | 344 | 525 | 344
EF-3 | HOOD |  |  |  |  | 1350 | 1260 | 0 | 0
TOTALS |  | 2400 | 2447 | 1050 | 966 | 2100 | 1846 | 750 | 586
HOODS ON
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 2400 | 2447 |  |  | FRONT |  | 0.002 |  | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2100 | 1846 |  |  | SIDE |  | 0.0022
NET AIRFLOW |  | 300 | 601 |  |  | REAR |  | 0.0035 |  | TRUE
[6 empty] | AVERAGE |  | 0.0025667
HOODS OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1050 | 966 |  |  | FRONT |  | 0.0242
TOTAL EXHAUST |  | 750 | 586 |  |  | SIDE |  | 0.0278
NET AIRFLOW |  | 300 | 380 |  |  | REAR |  | 0.0242
[6 empty] | AVERAGE |  | 0.0254
NOTES:
See issues list.