## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 6261 | 4200 | 4209 | 1950 | 2052 | 31.71% | 32.77%
RTU-2 | KITCHEN | 6150 | 5989 | 4250 | 3991 | 1900 | 1998 | 30.89% | 33.36%
PRV-1 | RESTROOMS | [12 empty] | 375 | 393
PRV-2 | HD1 GRIDDLE | [10 empty] | 1500 | 1554
PRV-3 | HD2 FRYER | [10 empty] | 1500 | 1622
PRV-4 | HD3 DISH | [10 empty] | 350 | 328
EF-1 | MOP ROOM | [12 empty] | 75 | 78
TOTALS |  | 12300 | 12250 | 8450 | 8200 | 3850 | 4050 |  |  | 0 | 0 | 3350 | 3504 | 450 | 471
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3850 | 4050 |  | FRONT |  | 0.006 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3800 | 3975 |  | SIDE |  | 0.006 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 75 |  | REAR |  | 0.005 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0056667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0