- RTU DINING

  - SET HEAT, COOL, VENTILATION TO SAME SPEED VIA PRODIGY CONTROLLER

    - INITIALLY THESE WERE ALL DIFFERENT SPEEDS

  - NEW PRODIGY BOARD

  - OA INITIALLY CLOSED

  - OPENED VIA PRODIGY SETTINGS

  - SET OA TO 22% (OPEN APPROX ¾”)

  - TRAVERSED DROP

    - 16”X33”

    - 780 FPM AVG

    - 2863 CFM TOTAL

  - LEAKAGE FOUND AT SUPPLY DROP

- RTU KITCHEN

  - VERY CLOSE TO KEF

    - COVERED IN GREASE

  - SET HEAT, COOL, VENTILATION TO SAME SPEED VIA PRODIGY CONTROLLER

    - INITIALLY THESE WERE ALL DIFFERENT SPEEDS

  - NO OUTSIDE AIR FILTERS

  - ECONOMIZER NOT FUNCTIONAL

  - MANUALLY OPENED OA DAMPERS APPROX 3/4”

  - OLD PRODIGY BOARD (WHITE)

  - READ VIA FLOW HOOD

    - 2650CFM TOTAL

- NEITHER RTU HAS HAIL GUARDS

- THERMOSTATS WERE SET TO AUTO FAN

  - CHANGED TO FAN ON

- WOMENS RR

  - 63CFM EXHAUST

  - 204CFM SUPPLY

- MENS RR

  - 76CFM EXHAUST

  - 175CFM SUPPLY

INITIAL CONDITIONS

- RTU SET TO VARIABLE SPEED

- NO OUTSIDE AIR

- THERMOSTATS SET TO AUTO FAN

ADJUSTMENTS MADE BEFORE TAKING MEASUREMENTS

- UNITS SET TO CONSTANT VOLUME

- OUTSIDE AIR OPENED APPROX ¾” AT EACH RTU

- THERMOSTATS SET TO FAN ON