## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  |  | 3986 | 0 | 2830 |  | 1156 | #DIV/0! | 29%
RTU-2 |  |  | 3800 | 0 | 3089 |  | 711 | #DIV/0! | 18.71%
MUA-1 | [10 empty] | 1679
KEF-1 | [12 empty] | 2877
EF-1 | MENS RR | [13 empty] | 76
EF-2 | WOMENS RR | [13 empty] | 63
TOTALS |  | 0 | 7786 | 0 | 5919 | 0 | 1867 |  |  | 0 | 1679 | 0 | 2877 | 0 | 139
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 0 | 3546 |  | FRONT |  | 0.0014 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 0 | 3016 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 530 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0014 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
BOTH RTU OA DAMPERS SET MANUALLY BUT NOT FULLY FUNCTIONAL. RECOMMEND SERVICING.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0