## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FRNT KITCHEN | 2000 | 2020 | 1800 | 1824 | 200 | 196 | 10% | 9.703%
RTU-2 | BACK KITCHEN | 2000 | 2101 | 1700 | 1770 | 300 | 331 | 15% | 15.75%
RTU-3 | DINING | 3000 | 3062 | 2340 | 2426 | 660 | 636 | 22% | 20.77%
MUA-1 | COOKLINE | [8 empty] | 1976 | 1998
KEF-1 | HOOD 1 | [10 empty] | 2381 | 2402
CEF-1 | UNISEX RR | [12 empty] | 100 | 107
CEF-2 | UNISEX RR | [12 empty] | 150 | 150
TOTALS |  | 7000 | 7183 | 5840 | 6020 | 1160 | 1163 |  |  | 1976 | 1998 | 2381 | 2402 | 250 | 257
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3136 | 3161 |  | FRONT |  | 0.0042 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2631 | 2659 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 505 | 502 |  | REAR |  | 0.0081 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00615 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0