## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5000 | 4993 | 3350 | 3383 | 1650 | 1610 | 33% | 32.25%
RTU-2 | KITCHEN | 3000 | 3076 | 2250 | 2299 | 750 | 777 | 25% | 25.26%
MUA-1 | KITCHEN | [8 empty] | 2800 | 2840
KEF-1 | HOOD1 | [10 empty] | 1500 | 1469
KEF-2 | HOOD2 | [10 empty] | 1500 | 1530
DEF-1 | HOOD3 | [10 empty] | 350 | 361
TEF-2 | TOILET | [12 empty] | 600 | 606
TOTALS |  | 8000 | 8069 | 5600 | 5682 | 2400 | 2387 |  |  | 2800 | 2840 | 3350 | 3360 | 600 | 606
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5200 | 5227 |  | FRONT |  | 0.0052 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3950 | 3966 |  | SIDE |  | 0.0072 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1250 | 1261 |  | REAR |  | 0.0063 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0062333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0