## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 27000 | 14964 | 21250 | 11397 | 5750 | 3567 | 21.3% | 23.84%
RTU-2 | DEPT. MGR LOUNGE | 700 | 360 | 700 | 360 | 0 | 0 | 0% | 0%
RTU-3 | FRONT OFFICES | 700 | 717 | 700 | 717 | 0 | 0 | 0% | 0%
RUT-DB | DELI/BAKERY | 2000 | 0 | 1800 | 0 | 200 | 0 | 10% | #DIV/0!
SF-1 | DELI HOOD | [8 empty] | 2100 | 0
EF-1 | RESTROOMS | [12 empty] | 750 | 0
EF-2 | RACK OVEN | [12 empty] | 750 | 0
EF-3 | LOUNGE | [12 empty] | 300 | 310
EF-4 | JANITOR AREA | [12 empty] | 200 | 0
HEF-1 | DELI | [10 empty] | 3300 | 0
TOTALS |  | 30400 | 16041 | 24450 | 12474 | 5950 | 3567 |  |  | 2100 | 0 | 3300 | 0 | 2000 | 310
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 8050 | 3567 |  | FRONT |  | 0.018 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 5300 | 310 |  | SIDE |  | 0.014 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 2750 | 3257 |  | REAR |  | 0.002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.011333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0