## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING ROOM | 3400 | 3250 | 0 | 2420 | 800 | 830 | 23.53% | 25.54%
RTU-2 | KITCHEN | 5000 | 4656 | 0 | 4170 | 500 | 486 | 10% | 10.44%
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
|  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
MAU-1 | HOOD MAKE UP | [8 empty] | 3045 | 3281
EF-1 | Grease Fan | [10 empty] | 2012 | 1880
EF-2 | Grease Fan | [10 empty] | 1794 | 1805
EF-3 | RESTROOM | [12 empty] | 350 | 362
TOTALS |  | 8400 | 7906 | 0 | 6590 | 1300 | 1316 |  |  | 3045 | 3281 | 3806 | 3685 | 350 | 362
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4345 | 4597 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 4156 | 4047 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 189 | 550 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0