## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTUX-1 | DINING | 4000 | 3933 | 3510 | 3454 | 490 | 479 | 12.25% | 12.18%
RTUX-2 | KITCHEN/BOH | 4000 | 4044 | 3590 | 3632 | 410 | 412 | 10.25% | 10.19%
MUA-1 | HOOD MAU | [8 empty] | 1976 | 1971
KEF-1 | HOOD FAN | [10 empty] | 2381 | 2312
EF-1 | RESTROOM | [12 empty] | 120 | 43
EF-2 | RESTROOM | [12 empty] | 120 | 52
EF-3 | MOP SINK | [12 empty] | 75 | 61
TOTALS |  | 8000 | 7977 | 7100 | 7086 | 900 | 891 |  |  | 1976 | 1971 | 2381 | 2312 | 315 | 156
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2876 | 2862 |  | FRONT |  | 0.0066 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2696 | 2468 |  | SIDE |  | 0.0024 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 180 | 394 |  | REAR |  | 0.0094 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0061333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0