## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FOOD SERVICE | 4500 | 4595 | 3800 | 3882 | 700 | 713 | 15.56% | 15.52%
RTU-2 | RETAIL | 3400 | 3348 | 3020 | 2617 | 380 | 731 | 11.18% | 21.83%
RTU-3 | FOH | 2400 | 2399 | 2200 | 1920 | 200 | 479 | 8.333% | 19.97%
EF-1 | RESTROOM | [12 empty] | 375 | 391
EF-2 | BOH | [12 empty] | 400 | 480
EF-3 | TRASH | [12 empty] | 200 | 230
TOTALS |  | 10300 | 10342 | 9020 | 8419 | 1280 | 1923 |  |  | 0 | 0 | 0 | 0 | 975 | 1101
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1280 | 1923 |  | FRONT |  | 0.006 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 975 | 1101 |  | SIDE |  | 0.005 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 305 | 822 |  | REAR |  | 0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0046667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
EF-2 has wrong motor according to new Change Initiative (CI). Supposed to reach 1100 TOTAL CFM. EF-3 has no speed controller installed, unable to decrease fan speed from MAX.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0