## RTU-1
National TAB
Project: Enterprise Rent-A-Car
Address: 9015 Fields Ertel Cincinnati, OH
Asset: RTU-1 (EXISTING)
Unit Data |  | Test Data
Manufacturer | NT COMFORT PRODUCTS |  | Design | Actual
Model Num | RGS090HECA0 | SF CFM | 2400 | 2469
Serial Num | P171740039 | SF RPM |  | 762
Configuration | VERTICAL | RA CFM | 2160 | 2240
Num OA Filters | 1 | OA CFM | 240 | 229
OA Filter Size | 4x10 | RL VOLTAGE |  | 212.2
Num Final Filter | 4 | RL AMPERAGE |  | 5.68
Final Filter Size | 20" X 20' X 2" | OA Damper Position |  | 100%
Motor Data |  | Performance Data
Motor MFG | MARATHON |  | Design | Actual
Frame | 56HY | Fan Suction SP |  | 0.76"
Horsepower | NA | Fan Discharge SP |  | 0.34"
Motor RPM | 1725 | Fan Total SP |  | 1.1"
Phase | 3 | DX Coil PD * |  | 0.37"
Rated Voltage | 208 | Pre Filter PD |  | *combined
Rated Amperage | 8.4 | Total ESP |  | 1.49"
Service Factor | 1
Drive Data
Motor Sheave Size / Bore | 4.0875 / 0.75"
Fan Sheave Size / Bore | 8.25 / 1"
Belt CL Distance | 17.25"
No. Belts / Size | 1 / AX51

## RTU-1 SGRD
National TAB
Project: Enterprise Rent-A-Car
Address: 9015 Fields Ertel Cincinnati, OH
Asset: SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-1 | 105 | SR | 28X4 | 100 | 139 | 108 | 1.08
1-2 | 105 | CD-8 | 8 | 125 | 178 | 129 | 1.032
1-3 | 100 | CD-10 | 10 | 350 | 206 | 337 | 0.96286
1-4 | RENTAL CTR | CD-10 | 10 | 325 | 271 | 340 | 1.0462
1-5 | RENTAL CTR | CD-10 | 10 | 325 | 310 | 328 | 1.0092
1-6 | 105 | SR | 28X4 | 150 | 99 | 140 | 0.93333
1-7 | 105 | SR | 28X4 | 150 | 175 | 155 | 1.0333
1-8 | 101 | CD-6 | 6 | 50 | 49 | 50 | 1
1-9 | 108 | SR | 8X4 | 50 | 53 | 51 | 1.02
1-10 | 103 | SR | 28X4 | 150 | 175 | 193 | 1.2867
1-11 | 106 | CD-8 | 8 | 150 | 172 | 154 | 1.0267
1-12 | 103 | SR | 28X4 | 125 | 187 | 133 | 1.064
1-13 | HALL | CD-6 | 6 | 100 | 118 | 97 | 0.97
1-14 | 104 | SR | 28X4 | 100 | 175 | 108 | 1.08
1-15 | 106 | CD-8 | 8 | 150 | 150 | 146 | 0.97333
|  |  |  | 2400 |  | 2469 | 1.0288

## EF-1
National TAB
Project: Enterprise Rent-A-Car
Address: 9015 Fields Ertel Cincinnati, OH
Asset: EF-1 |  | Area: 101
Unit Data
MFG | S&P USA
Model Num | PC110XP
Serial Num | 220808374
Type | CEILING
Motor Data
Motor MFG | INTERTEK
Frame | NA
Horsepower | 0.04
Motor Rpm | NA
Phase | 1
Voltage (rated) | 120
Amperage (rated) | 0.35
Service Factor | NA
Test Data
Design CFM | 89
Actual CFM | 85
-

## EF-2
National TAB
Project: Enterprise Rent-A-Car
Address: 9015 Fields Ertel Cincinnati, OH
Asset: EF-2 |  | Area: 107
Unit Data |  |  | Test Data
MFG | S&P USA |  |  | Design | Actual
Model Num | SDBDe8 |  | CFM | 600 | 641
Serial Num | 963173-1 |  | RL Voltage | 115 | 119
Type | CRE DNBLAST |  | RL Amperage |  | 1.8
|  |  | Suction ESP |  | 0.38
Motor Data |  |  | Total ESP | 0.5 | 0.38
Horsepower | 0.333
Motor Rpm | 1750
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 2.5
Service Factor | 1.15
-

## MAU-1
National TAB
Project: Enterprise Rent-A-Car
Address: 9015 Fields Ertel Cincinnati, OH
Asset: MAU-1 |  | Area: 107
Unit Data |  |  | Test Data
MFG | CAPTIVEAIRE |  |  | Design | Actual
Model Num | R76 |  | CFM | 600 | 654
Serial Num | 5947260 |  | RL Voltage | 115 | 120
|  |  | RL Amperage | 11.6 | 8.9
Motor Data |  |  | Brake Horse Power |  | 0.77
Horsepower | 1 | 1
Phase | 1 | 1
Voltage (rated) | 115 | 120
Amperage (rated) | 11.6 | 11.6