## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 8568 | 7000 | #VALUE! | 1750 | - | 20% | #VALUE!
AC-2 | DRIVE THRU | 1600 | 1602 | 1200 | 1220 | 400 | 382 | 25% | 23.85%
AC-3 | DINING | 6125 | 6322 | 4425 | 4740 | 1700 | 1582 | 27.76% | 25.02%
AC-4 | BOH | 1875 | 1793 | 1375 | 1324 | 500 | 469 | 26.67% | 26.16%
EF-1 | HOOD 1 | [10 empty] | 1913 | 1603
EF-2 | HOOD 2 & 3 | [10 empty] | 1402 | 1443
EF-3 | RR | [12 empty] | 300 | 281
TOTALS |  | 18350 | 18285 | 14000 | #VALUE! | 4350 | 2433 |  |  | 0 | 0 | 3315 | 3046 | 300 | 281
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 4350 | 2433 |  | FRONT |  | 0.003 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 3615 | 3327 |  | SIDE |  | 0.002 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 735 | -894 |  | REAR |  | 0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0026667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390