## SUMMARY (2)
AIR BALANCE SCHEDULE
|  | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT |  | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BREAKRM | 700 | 641 | 700 | 641 | 0 | 0 | 0% | 0%
RTU-2 | COOLER | 5600 | 4230 | 5600 | 4230 | 0 | 0 | 0% | 0%
RTU-3 | OFFICES | 1050 | 974 |  |  | 0 | 0 | 0% | 0%
RTU-4 | CHCKOUT | 7000 | 7324 |  |  |  |  | 0% | 0%
RTU-5 | SALES FLR | 7000 | 5831 | 6400 |  | 1600 |  | 22.86% | 0%
RTU-6 | BAKERY | - | 2496 | #VALUE! | 2496 |  |  | #VALUE! | 0%
RTU-7 | VESTIIBULE | 1050 | 939 | 1050 | 939 | 0 | 0 | 0% | 0%
RTU-8 | PRODUCE | 1400 | 1426 | 1400 | 1426 | 0 | 0 | 0% | 0%
RTU-9 | DELI | 5250 | 5336 | 5250 | 5336 |  |  | 0% | 0%
EF-1 | RR | [13 empty] | 410
EF-2 | MEAT | [11 empty] | 1024
EF-3 | DELI | [11 empty] | 1690
EF-5 | DELI | [11 empty] | 3315
EF-6 | BAKERY | [11 empty] | 364
EF-7 | BAKERY | [11 empty] | 1226
EF-8 | SEC. OFF | [13 empty] | 44
TOTALS |  | 29050 | 29197 | #VALUE! | 15068 | 1600 | 0 |  |  | 0 | 0 | 0 | 7619 | 0 | 454
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 1600 | 0 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | TRUE
TOTAL EXHAUST |  | 0 | 8073 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 1600 | -8073 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT |  |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0