## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 5851 | 4200 | 3851 | 1950 | 2000 | 31.71% | 34.18%
RTU-2 | KITCHEN | 6150 | 5942 | 4250 | 3980 | 1900 | 1962 | 30.89% | 33.02%
PRV-1 | RESTROOMS | [12 empty] | 375 | 398
PRV-2 | HD1 GRIDDLE | [10 empty] | 1500 | 1506
PRV-3 | HD2 FRYER | [10 empty] | 1500 | 1599
EF1-A | HD3 DISH | [10 empty] | 350 | 364
EF-1 | MOP ROOM | [12 empty] | 75 | 72
TOTALS |  | 12300 | 11793 | 8450 | 7831 | 3850 | 3962 |  |  | 0 | 0 | 3350 | 3469 | 450 | 470
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3850 | 3962 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3800 | 3939 |  | SIDE |  | 0.008 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 23 |  | REAR |  | 0.006 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0063333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0