## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8000 | 8107 | 6000 | 6046 | 2000 | 2061 | 25% | 25.42%
AC-2 | SIDE DINING | 2830 | 5942 | 2080 | 5248 | 750 | 694 | 26.5% | 11.68%
AC-3 | MAIN DINING | 5000 | 5191 | 3645 | 3758 | 1355 | 1433 | 27.1% | 27.61%
AC-4 | PLAY AREA | 1800 | 1770 | 1500 | 1494 | 300 | 276 | 16.67% | 15.59%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1931
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1403
EF-3 | RESTROOM | [12 empty] | 400 | 383
TOTALS |  | 17630 | 21010 | 13225 | 16546 | 4405 | 4464 |  |  | 0 | 0 | 3315 | 3334 | 400 | 383
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4405 | 4464 |  | FRONT |  | 0.015 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3715 | 3717 |  | SIDE |  | 0.015 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 690 | 747 |  | REAR |  | 0.011 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.013667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390