## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING AREA | 6000 | 0 | 4800 | 0 | 1200 | 0 | 20% | #DIV/0!
RTU-2 | KITCHEN | 3040 | 3052 | 2432 | 2460 | 608 | 592 | 20% | 19.4%
RTU-3 | BACKROOM | 1600 | 1495 | 1280 | 1185 | 320 | 310 | 20% | 20.74%
MUA-1 | HD-1 | [8 empty] | 2200 | 617
EF-1 | HD-1 | [10 empty] | 1800 | 1832
EF-2 | HD-1 | [10 empty] | 1800 | 1832
EF-3 | RESTROOMS | [12 empty] | NA | 0
TOTALS |  | 10640 | 4547 | 8512 | 3645 | 2128 | 902 |  |  | 2200 | 617 | 3600 | 3664 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 4328 | 1519 |  | FRONT |  | -0.05 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3600 | 3664 |  | SIDE |  | -0.08 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 728 | -2145 |  | REAR |  | NA | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.065 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
RTU-1 WAS OPERATIONAL BUT STOPPED WORKING TOWARDS THE END OF THE DAY. CFM AND PRESSURES REFLECT RTU-1 NOT OPERATIONAL.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0