## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 800 | 791 | 350 | 791
RTU-2 | SALES | 800 | 942 | 350 | 942
RTU-3 | BOH/KITCHEN | 800 | 798 | 350 | 785
EF-1 | RR/JANITOR |  |  |  |  | 750 | 704 | 750 | 704
EF-3 | KITCHEN HD |  |  |  |  | 1350 | 1398 | 0 | 297
TOTALS |  | 2400 | 2531 | 1050 | 2518 | 2100 | 2102 | 750 | 1001
HOODS ON
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 2400 | 2531 |  |  | FRONT |  | 0.004 |  | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2100 | 2102 |  |  | SIDE |  |  | 0.006
NET AIRFLOW |  | 300 | 429 |  |  | REAR |  |  | -0.004 | TRUE
[6 empty] | AVERAGE |  | 0.002
HOODS OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1050 | 2518 |  |  | FRONT
TOTAL EXHAUST |  | 750 | 1001 |  |  | SIDE
NET AIRFLOW |  | 300 | 1517 |  |  | REAR
AVERAGE
NOTES:
Economizer is only functional on RTU1, the other 2 OA setpoints had to be done manually, so there is no way for them to change with a difference in exhaust. Working economizer still had to be changed to a different setting manually for the OA damper to close. Economizer on RTU3 has power, and moves when manual setting changed; however, it did move RTU3's OA damper, so it was ultimately only adjusted by loosening the set screw and turning the gears.