## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FUR 1&2 | DINING | 2900 | 3043 | 1900 | 2008 | 1000 | 1035 | 34.48% | 34.01%
FUR 3&4 | KITCHEN | 3200 | 3119 | 2700 | 2641 | 500 | 478 | 15.62% | 15.33%
MUA-1 | KITCHEN HD | [8 empty] | 1300 | 1402
EF-1 | KITCHEN HD | [10 empty] | 2550 | 2609
EF-2&3 | RESTROOM | [12 empty] | 160 | 170
TOTALS |  | 6100 | 6162 | 4600 | 4649 | 1500 | 1513 |  |  | 1300 | 1402 | 2550 | 2609 | 160 | 170
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2915 |  | FRONT |  | 0.0026 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2710 | 2779 |  | SIDE |  | 0.0015 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 90 | 136 |  | REAR |  | 0.0009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0016667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0