## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 8562 | 8120 | 7057 | 1380 | 1505 | 14.53% | 17.58%
AC-2 | SERVING | 5600 | 4340 | 4325 | 3290 | 1275 | 1050 | 22.77% | 24.19%
AC-3 | RESTROOM | 6400 | 5985 | 4375 | 4037 | 2025 | 1948 | 31.64% | 32.55%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1932
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1277
EF-3 | RESTROOM | [12 empty] | 300 | 401
EF-4 | DTT CLOSET | [12 empty] | 450 | 473
TOTALS |  | 21500 | 18887 | 16820 | 14384 | 4680 | 4503 |  |  | 0 | 0 | 3314 | 3209 | 750 | 874
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4680 | 4503 |  | FRONT |  | 0.0048 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4064 | 4083 |  | SIDE |  | 0.0105 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 616 | 420 |  | REAR |  | 0.0071 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0074667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390