## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FOOD SERVICE | 4500 | 4598 | 3800 | 3882 | 700 | 716 | 15.56% | 15.57%
RTU-2 | RETAIL | 3650 | 3696 | 2970 | 3006 | 680 | 690 | 18.63% | 18.67%
RTU-3 | FOH | 2400 | 2428 | 1950 | 2005 | 450 | 423 | 18.75% | 17.42%
EF-1 | RESTROOM | [12 empty] | 375 | 327
EF-2 | BOH | [12 empty] | 1100 | 1117
EF-3 | TRASH | [12 empty] | 200 | 241
TOTALS |  | 10550 | 10722 | 8720 | 8893 | 1830 | 1829 |  |  | 0 | 0 | 0 | 0 | 1675 | 1685
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1830 | 1829 |  | FRONT |  | 0.015 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1675 | 1685 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 155 | 144 |  | REAR |  | 0.0093 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.01215 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0