## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4500 | 4295 | 2900 | 2635 | 1600 | 1660 | 35.56% | 38.65%
RTU-2 | DINING | 4500 | 4227 | 2900 | 2590 | 1600 | 1637 | 35.56% | 38.73%
EF-1 | HD1 GRILL | [10 empty] | 1200 | 1201
EF-2 | HD2 FRYER | [10 empty] | 1500 | 1425
EF-3 | RESTROOM | [12 empty] | 300 | 285
TOTALS |  | 9000 | 8522 | 5800 | 5225 | 3200 | 3297 |  |  | 0 | 0 | 2700 | 2626 | 300 | 285
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3200 | 3297 |  | FRONT |  | 0.0059 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3000 | 2911 |  | SIDE |  | 0.0087 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 200 | 386 |  | REAR |  | -0.0024 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0040667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0