## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | SIDE DINNING | 2000 | 1810 | 1500 | 1309 | 500 | 501 | 25% | 27.68%
AC-2 | DINNING | 4000 | 3856 | 3000 | 2846 | 1000 | 1010 | 25% | 26.19%
AC-3 | SERVING/DINNING | 3000 | 3188 | 2250 | 2494 | 750 | 694 | 25% | 21.77%
AC-4 | KITCHEN | 6400 | 6876 | 4400 | 4954 | 2000 | 1922 | 31.25% | 27.95%
AC-5 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1754
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1483
EF-3 | RESTROOM | [12 empty] | 400 | 378
TOTALS |  | 15400 | 15730 | 11150 | 11603 | 4250 | 4127 |  |  | 0 | 0 | 3315 | 3237 | 400 | 378
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4250 | 4127 |  | FRONT |  | 0.0007 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3715 | 3615 |  | SIDE |  | 0.0003 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 535 | 512 |  | REAR |  | 0.0009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00063333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Final Pressure was taken with hood 2 missing filters. Pressure will be more positive when filters are installed.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390