## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 800 | 836 | 350 | 337
RTU-2 | SALES | 800 | 808 | 350 | 351
RTU-3 | BOH/KITCHEN | 800 | 752 | 350 | 379
EF-1 | WOMEN'S RR |  |  |  |  | 225 | 220 | 225 | 220
EF-2 | MEN'S RR |  |  |  |  | 525 | 529 | 525 | 529
EF-3 | HOOD |  |  |  |  | 1350 | 1347 | 0 | 0
TOTALS |  | 2400 | 2396 | 1050 | 1067 | 2100 | 2096 | 750 | 749
HOODS ON
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 2400 | 2396 |  |  | FRONT |  | 0.0127 |  | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2100 | 2096 |  |  | SIDE |  | 0.0099
NET AIRFLOW |  | 300 | 300 |  |  | REAR |  | 0.0131 |  | TRUE
[6 empty] | AVERAGE |  | 0.0119
HOODS OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1050 | 1067 |  |  | FRONT |  | 0.0182
TOTAL EXHAUST |  | 750 | 749 |  |  | SIDE |  | 0.0211
NET AIRFLOW |  | 300 | 318 |  |  | REAR |  | 0.0156
[6 empty] | AVERAGE |  | 0.0183
NOTES: