## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | KITCHEN | 1600 | 1505 | 1290 | 1184 | 310 | 321 | 19.38% | 21.33%
AHU-2 | KITCHEN | 1600 | 1549 | 1290 | 1206 | 310 | 343 | 19.38% | 22.14%
AHU-3 | DINING | 1600 | 1631 | 1125 | 1159 | 475 | 472 | 29.69% | 28.94%
AHU-4 | DINING | 1600 | 1494 | 1125 | 1022 | 475 | 472 | 29.69% | 31.59%
EF-1 | KITCHEN/RR | [12 empty] | 1720 | 1638
TOTALS |  | 6400 | 6179 | 4830 | 4571 | 1570 | 1608 |  |  | 0 | 0 | 0 | 0 | 1720 | 1638
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1570 | 1608 |  | FRONT |  | -0.0017 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 1720 | 1638 |  | SIDE |  | 0.0014 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -150 | -30 |  | REAR |  | -0.0002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.00016667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0