## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
EX-FCU1 | MAIN BUILDING | 1255 | 1084 | 1055 | 877 | 200 | 207 | 15.94% | 19.1%
EX-FCU2 | EXAM RMS, OFFICES | 2140 | 1993 | 1890 | 1849 | 250 | 144 | 11.68% | 7.225%
EX-FCU3 | MAIN BUILDING | 1810 | 1612 | 1400 | 1479 | 410 | 133 | 22.65% | 8.251%
RTU-1 | ADDITION | 1600 | 1608 | 1200 | 1198 | 400 | 410 | 25% | 25.5%
NEW FCU | BREAKROOM | 630 | 635 | 472 | 359 | 158 | 276 | 25.08% | 43.46%
EF-1 | RESTROOM | [12 empty] | 75 | 93
EF-2 | ADDITION | [12 empty] | 365 | 376
EF-3 | SURGERY | [12 empty] | 275 | 420
EF-4 | CAT WARD | [12 empty] | 100 | 0
EF-5 | RESTROOM | [12 empty] | 75 | 73
EF-6 | DENTAL | [12 empty] | 175 | 186
EF-7 | TREATMENT | [12 empty] | 275 | 414
TOTALS |  | 7435 | 6932 | 6017 | 5762 | 1418 | 1170 |  |  | 0 | 0 | 0 | 0 | 1340 | 1562
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 1418 | 1170 |  | FRONT |  | -0.012 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 1340 | 1562 |  | SIDE |  | -0.0068 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 78 | -392 |  | REAR |  | -0.008 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0089333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
ROOM PRESSURES: SURGERY: +0.007", DOG WARD: -0.001", ISO: -0.009", CAT WARD: +0.0002"
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0