## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | KITCHEN | 1750 | 1805 | 1675 | 1723 | 75 | 82 | 4.286% | 4.543%
AHU-2 | SERVING | 1750 | 1773 | 1675 | 1693 | 75 | 80 | 4.286% | 4.512%
AHU-3 | DINING | 1750 | 1781 | 1375 | 1423 | 375 | 358 | 21.4% | 20.1%
AHU-4 | DINING | 1750 | 1794 | 1375 | 1429 | 375 | 365 | 21.43% | 20.35%
EF-1 | OVEN | [10 empty] | 850 | 847
EF-2 | RESTROOMS | [12 empty] | 150 | 156
TOTALS |  | 7000 | 7153 | 6100 | 6268 | 900 | 885 |  |  | 0 | 0 | 850 | 847 | 150 | 156
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 900 | 885 |  | FRONT |  | -0.001 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 1000 | 1003 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -100 | -118 |  | REAR |  | -0.002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0015 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0