## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3300 | 3428 | 2300 | 2454 | 1000 | 974 | 30.3% | 28.41%
RTU-2 | KITCHEN | 4600 | 4508 | 2400 | 2219 | 2200 | 2289 | 47.83% | 50.78%
FCU-1 | MANAGERS OFFICE |  |  |  |  | 40 | 39 | - | -
KEF-1 | HOOD 1 | [10 empty] | 1250 | 1260
KEF-2 | HOOD 2 | [10 empty] | 1238 | 1248
EF-1 | RESTROOMS | [12 empty] | 300 | 297
TOTALS |  | 7900 | 7936 | 4700 | 4673 | 3240 | 3302 |  |  | 0 | 0 | 2488 | 2508 | 300 | 297
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3240 | 3302 |  | FRONT |  | 0.0098 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2788 | 2805 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 452 | 497 |  | REAR |  | 0.0083 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00905 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2240 | 2328
TOTAL KITCHEN EXHAUST |  | 2488 | 2508
NET AIRFLOW |  | -248 | -180
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0