## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 | 8109 | 6375 | 6261 | 1750 | 1848 | 21.54% | 22.79%
AC-2 | DRIVE-THRU | 4375 | 4589 | 3300 | 3566 | 1075 | 1023 | 24.57% | 22.29%
AC-3 | DINING | 5250 | 5260 | 3975 | 4052 | 1275 | 1208 | 24.29% | 22.97%
AC-4 | OFFICE/TEAM MEMBER | 1750 | 1814 | 1325 | 1403 | 425 | 411 | 24.29% | 22.66%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1893
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1401
EF-3 | RESTROOM | [12 empty] | 300 | 310
EF-4 | RESTROOM | [12 empty] | 75 | 75
TOTALS |  | 19500 | 19772 | 14975 | 15282 | 4525 | 4490 |  |  | 0 | 0 | 3315 | 3294 | 375 | 385
[16 empty] | TRUE | FALSE | FALSE
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1 | TRUE | FALSE | FALSE
TOTAL OA |  | 4525 | 4490 |  | FRONT |  | 0.004
TOTAL EXHAUST |  | 3690 | 3679 |  | SIDE |  | 0.004 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1 | TRUE
NET AIRFLOW |  | 835 | 811 |  | REAR |  | 0.009
[5 empty] | AVERAGE |  | 0.0056667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390