Mark’s Feed Store Summary

- Initially observed severely negative building pressure (-0.253” average).

- MUA filters are overly dirty along with plenum preventing MUA from delivering the correct amount of air to kitchen.

- All economizers for each RTU were 100% closed. Looked further and observed that wire was not landed in occupied port on thermostat strip. Installed jumper ensuring economizer damper functions as designed. Increased net airflow from -3501 CFM to -250 CFM.

- Building pressure shifted from -0.253” to -0.074”.

- Recommend deep cleaning of MUA plenum.

- Recommend installation of transfer grilles connecting entry vestibule to rest of space, neutralizing pressure inside vestibule