Building Pressure was 0.07” on arrival.

MUA: Has Swamp cooler attached and is horizontal discharge into rooftop ductwork that connects to two diffusers, one in front of each hood, and then into RTU-2 (dining) OA. Diffuser in front of HD-1 is not connected and discharging into the ceiling. Swamp cooler has internal filter media that needs replacement. Building was 0.06” with unit running. Unit was left off.

RTU-1: Unit is 7.5 ton unit and is low on airflow. (2499/3000cfm).

- Filters need replacement (filter media)

- Evap coil dirty

- Motor sheave frozen (unable to adjust, estimated 1 turn open)

- Diffusers and return needs cleaning.

- Economizer not functional (not wired for occupancy)

RTU-2: Unit is 12.5 tons and is low on airflow. (3338/5000 cfm).

- Filters need replacement, dirty and wrong size.

- Motor sheave frozen (unable to adjust, set key missing, estimated 1.5 turn open)

- Diffusers and return needs cleaning.

- Economizer not functional (jumpered for occupancy)

KEF-1: Low on airflow, Rotation Incorrect.

- HD filters extremely dirty

- Grease Duct needs cleaning

KEF-2: High on airflow, unable to adjust speed (3 spd motor), rats nest of wiring, looks to be in high speed.

- HD filter needs replacement/cleaning. Exhaust airflow 919 with filter in, 2490 with it removed.

Restroom Exhaust:

Both fans in need of cleaning, womens RR fan not operating.

There is another ceiling fan installed by the roof ladder in BOH. Not operating, unsure of purpose.