## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3000 | 3010 | 2398 | 2391 | 602 | 619 | 20.07% | 20.56%
RTU-2 | DINING 2 | 3000 | 2920 | 2399 | 2331 | 601 | 589 | 20.03% | 20.17%
DOAS-1 | KITCHEN | 2250 | 2323 | 0 | 0 | 2250 | 2323 | 100% | 100%
KEF-1 | GRIDDLE | [10 empty] | 1600 | 1539
KEF-2 | FRYER | [10 empty] | 775 | 773
EF-1 | RR | [12 empty] | 150 | 145
EF-2 | RR | [12 empty] | 150 | 164
TOTALS |  | 8250 | 8253 | 4797 | 4722 | 3453 | 3531 |  |  | 0 | 0 | 2375 | 2312 | 300 | 309
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3453 | 3531 |  | FRONT |  | 0.0027 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2675 | 2621 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 778 | 910 |  | REAR |  | 0.0017 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0022 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0