## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 2400 | 2432 | 2050 | 2060 | 350 | 372 | 14.58% | 15.3%
RTU-2 | DINING | 2400 | 2380 | 2050 | 2007 | 350 | 373 | 14.58% | 15.67%
MUA-1 | KITCHEN | [8 empty] | 1699 | 1687
KEF-1 | HOOD | [10 empty] | 2117 | 2157
EF-2 | RESTROOM | [12 empty] | 120 | 122
EF-3 | RESTROOM | [12 empty] | 120 | 127
TOTALS |  | 4800 | 4812 | 4100 | 4067 | 700 | 745 |  |  | 1699 | 1687 | 2117 | 2157 | 240 | 249
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2399 | 2432 |  | FRONT |  | 0.0025 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2357 | 2406 |  | SIDE |  | 0.0012 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 42 | 26 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00185 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0