## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3290 | 2900 | 2747 | 500 | 543 | 14.71% | 16.5%
RTU-2 | DINING | 4000 | 3970 | 3000 | 2916 | 1000 | 1054 | 25% | 26.55%
MUA-1 | KITCHEN HOOD | [8 empty] | 1300 | 1261
EF-1 | KITCHEN HOOD | [10 empty] | 2550 | 2420
EF-2 | RESTROOM | [12 empty] | 150 | 153
TOTALS |  | 7400 | 7260 | 5900 | 5663 | 1500 | 1597 |  |  | 1300 | 1261 | 2550 | 2420 | 150 | 153
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2858 |  | FRONT | [10 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2700 | 2573 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 285 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | NOTE |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250