## RTU-1
National TAB
Project: EGLIN AFB (DESTIN, FL)
Address: Eglin AFB, FL 32542
Asset: RTU-1 |  | Area: BUILDING 525
Unit Data |  |  | Test Data
Manufacturer | Captive Aire |  |  | Design | Actual
Model Num | CASRTU1-E.302-16-7.5T |  | SF CFM | 2600 | 2530
Serial Num | 5999708 |  | SF RPM | 1051 | 90%
Configuration | RTU - HORIZONTAL |  | RA CFM | 2150 | 2059
Num OA Filters | 2 |  | OA CFM | 450 | 471
OA Filter Size | 16X20X2 |  | RL VOLTAGE | 208 | 211/210/212
Num PreFilter | 4 |  | RL AMPERAGE |  | 2.4/2.4/2.5
PreFilter Size | 16X16X2 |  | OA Damper Position |  | 5.0 V / 19%
|  |  | Brake Horsepower |  | N/A
Motor Data |  |  | Performance Data
Motor MFG | ZIEHL-ABEGG |  |  | Design | Actual
Frame | N/L |  | Fan Suction SP |  | -1.25
Horsepower | 2.5 |  | Fan Discharge SP |  | 1.01
Motor RPM | N/L |  | Fan Total SP |  | 2.26
Phase | 3 |  | DX Coil PD * |  | 0.610
Rated Voltage | 208 |  | Pre Filter PD |  | 0.196
Rated Amperage | 5.7 |  | Total ESP | 0.75 | 1.45 | MA | -0.44
Service Factor | N/L |  | DX Coil DB EAT |  | 76.6F
|  |  | DX Coil DB LAT |  | 59.6F
INDOOR TEMPS |  |  | DX Coil WB EAT |  | 64.9F
CURRENT TEMP. | 75.3F |  | DX Coil WB LAT |  | 57.3F
HUMIDITY | 54.4% RH |  | DX Coil Capacity |  | 7.5T
WETBULB | 64.0F
OUTDOOR TEMPS
CURRENT TEMP. | 97.3F
HUMIDITY | 53.4% RH
WETBULB | 82.2F
DEWPOINT | 77.8F

## RTU-2
National TAB
Project: EGLIN AFB (DESTIN, FL)
Address: Eglin AFB, FL 32542
Asset: RTU-2 |  | Area: BUILDING 525
Unit Data |  |  | Test Data
Manufacturer | Captive Aire |  |  | Design | Actual
Model Num | CASRTU1-E.152-13-5T |  | SF CFM | 1800 | 1744
Serial Num | 5999708 |  | SF RPM | 1095 | 2146
Configuration | RTU |  | RA CFM | 1650 | 1600
Num OA Filters | 2 |  | OA CFM | 150 | 144
OA Filter Size | 16X20X2 |  | RL VOLTAGE | 208 | 208/209/210
Num PreFilter | 4 |  | RL AMPERAGE |  | 5.0/5.0/4.9
PreFilter Size | 16X16X2 |  | OA Damper Position |  | 4.0V / 13%
|  |  | Brake Horsepower |  | 1.81
Motor Data |  |  | Performance Data
Motor MFG | TECO WESTINGHOUSE |  |  | Design | Actual
Frame | 145T |  | Fan Suction SP |  | -0.91
Horsepower | 2 |  | Fan Discharge SP |  | 0.63
Motor RPM | 1740 |  | Fan Total SP |  | 1.54
Phase | 3 |  | DX Coil PD * |  | 0.478
Rated Voltage | 230/460 |  | Pre Filter PD |  | 0.148 | MA | -0.25
Rated Amperage | 5.48/2.74 |  | Total ESP | 0.5 | 0.88
Service Factor | 1.15 |  | DX Coil DB EAT |  | 76.6F
|  |  | DX Coil DB LAT |  | 61.3F
INDOOR TEMPS |  |  | DX Coil WB EAT |  | 64.4F
CURRENT TEMP. | 75.9F |  | DX Coil WB LAT |  | 57.2F
HUMIDITY | 63.2% RH |  | DX Coil Capacity |  | 5T
WETBULB | 67.8F
OUTDOOR TEMPS
CURRENT TEMP. | 97.3F
HUMIDITY | 53.4% RH
WETBULB | 82.2F
DEWPOINT | 77.8F

## EF-1
National TAB
Project: EGLIN AFB (DESTIN, FL)
Address: Eglin AFB, FL 32542
Asset: EF-1 |  |  | Area: BUILDING 525
Unit Data |  |  |  |  | Test Data
MFG |  | AIR KING |  |  |  | Design | Actual
Model Num |  | AK280LS |  |  | CFM | 250 | 229
Serial Num |  | 3213221a |  |  | Fan RPM | 2050 | MAXIMIZED
Type |  | CEILING |  |  | RL Voltage | 120 | 121
[5 empty] | RL Amperage | 1.5 | 0.25
Motor Data |  |  |  |  | Suction ESP |  | -0.016
Motor MFG |  | N/L |  |  | Total ESP | 0.01 | 0.376"
Frame |  | N/L |  |  | Discharge ESP |  | 0.36"
Horsepower |  | N/L
Motor Rpm |  | N/L
Phase |  | 1
Voltage (rated) |  | 120
Amperage (rated) |  | 0.9
Service Factor |  | N/L
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-2
National TAB
Project: EGLIN AFB (DESTIN, FL)
Address: Eglin AFB, FL 32542
Asset: EF-2 |  |  | Area: BUILDING 525
Unit Data |  |  |  |  | Test Data
MFG |  | AIR KING |  |  |  | Design | Actual
Model Num |  | AK280LS |  |  | CFM | 250 | 228
Serial Num |  | 3213221a |  |  | Fan RPM | 2050 | MAXIMIZED
Type |  | CEILING |  |  | RL Voltage | 120 | 121
[5 empty] | RL Amperage | 1.5 | 0.21
Motor Data |  |  |  |  | Suction ESP |  | -0.01
Motor MFG |  | N/L |  |  | Total ESP | 0.01 | 0.32"
Frame |  | N/L |  |  | Discharge ESP |  | 0.31"
Horsepower |  | N/L
Motor Rpm |  | N/L
Phase |  | 1
Voltage (rated) |  | 120
Amperage (rated) |  | 0.9
Service Factor |  | N/L
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
-

## EF-A
National TAB
Project: EGLIN AFB (DESTIN, FL)
Address: Eglin AFB, FL 32542
Asset: EF-A |  |  | Area: BUILDING 535
Unit Data |  |  |  |  | Drive Data
MFG |  | PENNBARRY |  |  | Motor Sheave Size | MVL40B
Model Num |  | D10 |  |  | Motor Bore Size | 5/8"
Serial Num |  | H23TZ87101 |  |  | Fan Sheave Size | AL74
Type |  | CENTRIFUGAL - UPBLAST |  |  | Fan Bore Size | 3/4"
[5 empty] | Belt CL Distance | 8 3/8"
Motor Data |  |  |  |  | No of Belts | 1
Motor MFG |  | WEG |  |  | Belt Size | 4L330
Frame |  | W56
Horsepower |  | 0.25 |  |  | Test Data
Motor Rpm |  | 1735 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 350 | 362
Voltage (rated) |  | 115/208-230 |  |  | Fan RPM |  | 819
Amperage (rated) |  | 4.60/2.54-2.30 |  |  | RL Voltage | 120 | 119.8
Service Factor |  | 1.15 |  |  | RL Amperage |  | 4.58
[5 empty] | Suction ESP |  | -0.22
[5 empty] | Total ESP | 0.25 | 0.22
[5 empty] | Brake Horse Power |  | 0.25
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
Duct1 | H1 | Duct | 4 | 115 | 119 | 131 | 1.1391 | no dampers
Duct2 | H2 | Duct | 4 | 115 | 100 | 110 | 0.95652
Duct3 | H3 | Duct | 4 | 120 | 110 | 121 | 1.0083
|  |  |  | 350 | 329 | 362 | 1.0343
-

## EF-B
National TAB
Project: EGLIN AFB (DESTIN, FL)
Address: Eglin AFB, FL 32542
Asset: EF-B |  |  | Area: BUILDING 535
Unit Data |  |  |  |  | Drive Data
MFG |  | PENNBARRY |  |  | Motor Sheave Size | MVL40B
Model Num |  | D10 |  |  | Motor Bore Size | 5/8"
Serial Num |  | H23TZ87100 |  |  | Fan Sheave Size | AL74
Type |  | CENTRIFUGAL - UPBLAST |  |  | Fan Bore Size | 3/4"
[5 empty] | Belt CL Distance | 8 1/8"
Motor Data |  |  |  |  | No of Belts | 1
Motor MFG |  | WEG |  |  | Belt Size | 4L330
Frame |  | W56
Horsepower |  | 0.25 |  |  | Test Data
Motor Rpm |  | 1735 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 350 | 366
Voltage (rated) |  | 115/208-230 |  |  | Fan RPM |  | 848
Amperage (rated) |  | 4.60/2.54-2.30 |  |  | RL Voltage | 120 | 119
Service Factor |  | 1.15 |  |  | RL Amperage |  | 4.46
[5 empty] | Suction ESP |  | 0.27"
[5 empty] | Total ESP | 0.25 | 0.27"
[5 empty] | Brake Horse Power |  | 0.24
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
Duct1 | H4 | Duct | 4 | 115 | 120 | 120 | 1.0435
Duct2 | H5 | Duct | 4 | 115 | 116 | 116 | 1.0087
Duct3 | H6 | Duct | 4 | 120 | 130 | 130 | 1.0833
|  |  |  | 350 | 366 | 366 | 1.0457
-