## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4000 | 4182 | 2950 | 3111 | 1050 | 1071 | 26.25% | 25.61%
RTU-2 | KITCHEN | 4850 | 4120 | 2465 | 1809 | 2385 | 2311 | 49.18% | 56.09%
KEF-1 | HOOD 1 | [10 empty] | 1385 | 1393
KEF-2 | HOOD 2 | [10 empty] | 1400 | 1404
EF-1 | RESTROOMS | [12 empty] | 300 | 296
TOTALS |  | 8850 | 8302 | 5415 | 4920 | 3435 | 3382 |  |  | 0 | 0 | 2785 | 2797 | 300 | 296
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3435 | 3382 |  | FRONT |  | 0.0045 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3085 | 3093 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 350 | 289 |  | REAR |  | 0.0032 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00385 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2385 | 2311
TOTAL KITCHEN EXHAUST |  | 2785 | 2797
NET AIRFLOW |  | -400 | -486
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0