## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8500 | 7351 | 6500 | 5429 | 2000 | 1922 | 23.53% | 26.15%
AC-2 | SIDE DINING | 2830 | 2722 | 2080 | 1900 | 750 | 822 | 26.5% | 30.2%
AC-3 | DINING | 4000 | 4021 | 3000 | 3010 | 1000 | 1011 | 25% | 25.14%
AC-4 | DINING | 2765 | 2961 | 2165 | 2346 | 600 | 615 | 21.7% | 20.77%
AC-5 | PLAY AREA | 1800 | 1805 | 1500 | 1477 | 300 | 328 | 16.67% | 18.17%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 2000
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1314
EF-3 | RESTROOM | [12 empty] | 400 | 365
TOTALS |  | 19895 | 18860 | 15245 | 14162 | 4650 | 4698 |  |  | 0 | 0 | 3314 | 3314 | 400 | 365
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4698 |  | FRONT |  | 0.007 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3714 | 3679 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 936 | 1019 |  | REAR |  | 0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.005 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390