Lawrenceburg High School

Hot Water Balance Summary

12/01/2023

Scope of work includes (2) pumps, (4) boilers and all associated new devices. Before balancing all new hot water valves were commanded 100% open by Honeywell, existing valves left in auto, not closed. The pumps were turned off, static pressure read in the piping system, and water was added to reach the height of the building in relation to available FT/HD with the system off. Both pumps were “dead-headed” by closing discharge and recording differential head pressure. This method is used to determine the impeller size of the pumps matches design. Both pumps were placed in hand and driven to 60hz. Differential head pressures were measured, and motor speeds were set to remain at 60hz for duration of balancing. Upon arrival the system was running one pump at a time. This was changed to have both pumps at the same speed at all times per the sequence of operations. Balancing in the space began but discovered to be insufficient on all floors except the first floor. Per direction, NTAB tried closing all AHUs to force water to the 2nd 3rd and 4th floors but witnessed no change. Discovered that units with 3-way valves were bypassing water back to the pumps. One “chillet” bypass valve, roughly 1-1.5”, was located and closed in the basement. This did not produce any significant change to the system. A larger, roughly 2-2.5” bypass valve was located below existing RTU-2 (not in scope) and believed to be consuming the majority of any extra flow produced. Once this was closed, all floors are now receiving proportional amounts of flow with no issues of reheating to any devices with the exception of a small handful of assets (listed below) believed to need minor backflushing. Final 2/3 pressure setpoint recorded as 26 PSID with the conditions above present: (2) pumps running full speed, all new valves commanded to 100%, both bypasses listed above CLOSED.