## Sheet1
APPENDIX *RTU (ROOFTOP UNIT) *EH (ENTRY HEATER) *ERV (ENERGY RECOVERY VENTILATOR) *EF (EXHAUST FAN) *CU (SPLIT SYSTEM- COMPRESOR UNIT) *AHU(SPLIT SYSTEM-AIR HANDLER) |  |  | WALGREENS FY24 HVAC SITE SURVEY CHECKLIST
Date: | 2024-08-05 | Store#: | 5460 | Address: | 1001 W Reynolds St | Pontiac | IL | 61764
| EQUIPMENT DATA | [7 empty] | COOLING | HEATING |  | SMOKE DETECTOR |  | POWER SUPPLY |  |  |  | RTU/ROOF |  |  | CURB MEASUREMENTS
RTU DATA | Area Served (LOCATION) EX: Front Sales Pharmacy Storage PARTNER SPACE etc | DATE OF MFG. | EF (ROOF MOUNTED/IN-LINE) | MAKE | MODEL # | SERIAL # | INTERNAL & EXTERNAL UNIT CONDITION COMMENTS & NOTES: (*Give Full Details On Each Unit*) |  | CAPACITY TONS | HEAT TYPE PROPANE / NATURAL GAS / ELECTRIC / HEAT PUMP - AUX HEAT KW | HEATING CAPACITY MAX INPUT(BTU / KW) | LOCATION (UNIT / DUCT) | DUCT LOCATION (SUPPLY / RETURN) | GFI POWERED (Y/N) (BLDG. / RTU) | VOLTAGE (NAMEPLATE) | VOLTAGE (MEASURED) | PHASE | IF NEAREST EDGE OF RTU IS <10' FROM THE EDGE OF THE ROOF PROVIDE DISTANCE BETWEEN THE TWO EDGES (in) | DOES ROOF HAVE A PARAPET? (Y/N) | DOES RTU/HVAC EQUIPMENT UTALIZE OSHA ROOFTOP GUARD RAILS? (Y/N) | EXISTING CURB ADAPTER (YES/NO) | CURB MEASUREMENTS O.D. | UNIT MEASUREMENTS O.D.
RTU 1 | FRONT SALES | 1999-09-01 | ROOF | TRANE | YCD121C3HAA | P39103427D | Significant Hail damage on Condenser coils |  | 10 | NATURAL GAS | 203000 | DUCT | RETURN | Y | 208 | 200.8 | 3 | NA | Y | N | N | 103x65 | 71x107
RTU 2 | FRONT SALES | 1999-10-01 | ROOF | TRANE | YCD151C3HAAA | P39103503D | Significant Hail damage on Condenser coils |  | 12.5 | NATURAL GAS | 203000 | DUCT | RETURN | Y | 208 | 201.9 | 3 | NA | Y | N | N | 103x65 | 71x107
RTU 3 | BACKSALES | 1999-10-01 | ROOF | TRANE | YCD091D3HABE | P39102717D | Significant Hail damage on Condenser coils/Top RTU Cover loose/Bent. MA/ELECTRIC doors in poor condition. blower belt needs replacement |  | 7.5 | NATURAL GAS | 166000 | DUCT | RETURN | Y | 208 | 200 | 3 | NA | Y | N | N | 46x81.5 | 87x50
RTU 4 | BACK SALES | 1999-10-01 | ROOF | TRANE | YCD091D3HABE | P39102710D | Significant Hail damage on Condenser coils. not opertional. missing outdoor fan cover. |  | 5 | NATURAL GAS | 97200 | DUCT | RETURN | Y | 208 | 0 | 3 | 106" | Y | N | N | 82x47 | 87x50
RTU 5 | PHARMACY | 1999-10-01 | ROOF | TRANE | YCD061C3HABF | P3102840D | Significant Hail damage on Condenser coils. Unit not operational |  | 5 | NATURAL GAS | 166000 | DUCT | RETURN | Y | 208 | 0 | 3 | NA | Y | N | N | 81x45 | 87x50
RTU 6 | STOCK ROOM | 1999-10-01 | ROOF | TRANE | YCD037C3HABE | P39102610D | Significant Hail damage on Condenser coils. unit not operational |  | 3 | NATURAL GAS | 97200 | DUCT | RETURN | Y | 208 | 0 | 3 |  | Y | N | N | 81x45 | 87x50
RTU 7
EH | FRONT VESTIBULE | NL | ROOF | REZNOR | NL | NL |  |  | NL | NATURAL GAS | NL | NA | NA | N | NL | 0 | NL | 80" | Y | N | N | 85x35 | 87x39.5
SPLIT SYSTEM DATA
CU 1 | [6 empty] | *include line set sizes*
CU 2 | [6 empty] | *include line set sizes*
CU 3 | [6 empty] | *include line set sizes*
AHU 1
AHU 2
AHU 3
EVAPORATIVE COOLER/SWAMP COOLER
VENTILATION DATA
ERV 1
ERV 2
STOCK ROOM SF
STOCK ROOM EF
EF 1 | BREAK ROOM | NA | CEILING/INLINE | BROAN | 99H | NA | Significant blower dirt buildup | [6 empty] | NOT APPLICABLE | 120 | NO ACCESS | 1
EF 2 | MENS RR |  | CEILING/INLINE | NOT VISIBLE | NOT VISIBLE | NOT VISIBLE | Significant blower dirt buildup | [6 empty] | NOT APPLICABLE | NOT VISIBLE | NO ACCESS | NOT VISIBLE
EF 3 | WOMENS RR |  | CEILING/INLINE | NOT VISIBLE | NOT VISIBLE | NOT VISIBLE | Significant blower dirt buildup | [6 empty] | NOT APPLICABLE | NOT VISIBLE | NO ACCESS | NOT VISIBLE
EF 4 | OFFICE |  | CEILING/INLINE | NOT VISIBLE | NOT VISIBLE | NOT VISIBLE | Significant blower dirt buildup | [6 empty] | NOT APPLICABLE | NOT VISIBLE | NO ACCESS | NOT VISIBLE
EF 5
EF 6
EF 7
General Store Notes | [6 empty] | Electrical Panel Information | FUSED SWITCH OR BREAKER | FUSE / BREAKER BRAND | FUSE / BREAKER MODEL # | RATING(AMPS) | WIRE SIZE | CONDUIT SIZE AT UNIT
Former Rite Aid (Y/N): | N | [5 empty] | RTU-1 | FUSE | LITTELFUSE/SIEMENS | FLNR60ID | 60 | 4 | 1"
Partner Tenant (included but not lmited to: ex. Village Medical (VMD), LabCorp, Novant, and MedExpress) |  | NONE | Provid partner name |  |  |  | RTU-2 | FUSE | LITTELFUSE/SIEMENS | FLNR60ID | 60 | 4 | 1"
If Partner Tenant Exists do they have full height walls? (Y/N) |  | N | Full height walls are defined as walls up to ceiling. |  |  |  | RTU-3 | FUSE | LITTELFUSE/SIEMENS | FLNR60ID | 60 | 6 | 1"
Obvious "non-typical" Heat Load (Y/N) provide detail in note section |  | N | Ex.: Floor to glass windows, Sky Lights, Permanent Heat Productin Displays, Etc (please make high level note of any potential items.) |  |  |  | RTU-4 | FUSE | FUSETRON/SIEMENS | FRN-R-60 | 60 | 6 | 1"
Tenant Space (Y/N): | N |  | Tenant Name (VMD/Kroger/LabCorp, etc.):
Photo Lab (Y/N): | Y |  | Dry/Wet Lab: Dry |  |  |  | RTU-5 | FUSE | FUSETRON/SIEMENS | FRN-R-60 | 60 | 6 | 1"
Roof Condition (Good/Fair/Poor): | Fair | [5 empty] | RTU-6 | FUSE | LITTELFUSE/SIEMENS | FLNR60ID | 60 | 6 | 1"
Ductwork Type (Galvanized, Duct Board, Sock Duct, Other) | NO ACCESS |  | If "Other" Specify Type: |  |  |  | RTU-7
Unit Hail Damage (Y/N): | Y | [5 empty] | CU 1
Store within 20 Miles of Ocean? (Y/N): | N | [5 empty] | CU 2
Existing EMS (Y/N): | Y |  | EMS Type(FSG/Gridpoint): Gridpoint |  |  |  | CU 3
Fire Alarm Panel Operational (Y/N): | Y |  | Panel Model#:5207 |  |  |  | AHU 1
Photo of Fire Alarm Panel Taken (Y/N): | Y | [5 empty] | AHU 2
Main Refrigeration Type (Remote Condensing Unit or Self-Contained) | REMOTE | [5 empty] | AHU 3
Main Refridgeration Type (Walk-In or Reach-In) | Freezer: Walk In | [5 empty] | EVAPORATIVE COOLER/SWAMP COOLER
| Cooler Walk-In | [5 empty] | STOCK ROOM SF
Self-Contained Refrigeration ONLY Door Count: | Freezer: | [5 empty] | STOCK ROOM EF
Cooler:
Obvious Visual Damage to MDP (Y/N): | N |  | Explain Visual Damage:
Notes for Installer:
Original Curb Dimensional Data
RTU# | RTU1 | RTU2 | RTU3 | RTU4 | RTU5 | RTU6 | RTU7 | EH
Curb Type
A (Length)
B (Width)
E
F
G
H
I
J
K
L
M
N
O