## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5200 | 5014 | 4300 | 4164 | 900 | 850 | 17.31% | 16.95%
RTU-2 | KITCHEN | 5000 | 5109 | 4050 | 4112 | 950 | 997 | 19% | 19.51%
RTU-OA | RTU 1 & 2 | 3250 | 3157 | 1250 | 1059 | 2000 | 2098 | 61.54% | 66.46%
PRV-2 | HOOD 2 | [10 empty] | 1500 | 1499
PRV-3 | HOOD 1 | [10 empty] | 1500 | 1522
PRV-4 | HOOD 3 | [10 empty] | 350 | 0
EF-1 | RESTROOM | [12 empty] | 220 | 212
EF-2 | MOP ROOM | [12 empty] | 50 | 54
EF-3 | RESTROOM | [12 empty] | 70 | 68
TOTALS |  | 13450 | 13280 | 9600 | 9335 | 3850 | 3945 |  |  | 0 | 0 | 3350 | 3021 | 340 | 334
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1 | TRUE | FALSE | FALSE
TOTAL OA |  | 3850 | 3945 |  | FRONT |  | 0.0117
TOTAL EXHAUST |  | 3690 | 3355 |  | SIDE |  | 0.0013 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1 | TRUE | FALSE | FALSE
NET AIRFLOW |  | 160 | 590 |  | REAR |  | 0.0108
[5 empty] | AVERAGE |  | 0.0079333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1 | TRUE
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0